## bore discharge
version: 1.1. | [5 empty] | © 2012 Damian Janicki
|  | YourSpreadsheets™ 2nd Floor, 52 Marcus Hill, London www.YourSpreadsheets.co.uk Tel: 020 7542 8734 |  |  |  |  | Margery Street
Revision
[7 empty] | Job No: | 22668 |  | Page: | C/01
| Section: | Something Somewhere |  |  |  |  | Prepared By: | DJ |  | Date: | 2012-07-26
| PIPE DATA |  |  |  | CONSTANTS
| internal diameter of pipe 'D' [mm] = |  |  | 600 | gravitational acceleration 'g' [m/s2] = |  |  |  | 9.81
| effective roughness value 'Ks' [mm] = |  |  | 0.6 | kinematic viscosity of water 'μ' [m2/s] = |  |  |  | 1.31*10-6
| reduced bore discharge factor 'γ' = |  |  | 0.75 | NOTE: kinematic viscosity is for water at 10oC
PIPELINE DATA
| pipe length 'L' [m] = |  |  | 100
|  |  | invert level at beginning of pipe 'h1' [m] = | 14
|  |  | invert level at end of pipe 'h2' [m] = | 10
| hydraulic gradient 'i' [m/m] = |  |  | 0.04
| pipeline slope 's' : |  |  | 25
VELOCITY OF WATER
V = -2 * (2*9.81*0.6)^0.5 * log((0.0006/3.7*0.6) + (2.51*1.31*(10^-6) / 0.6*(2*9.81*0.6*0.04)))
| VELOCITY OF WATER 'V' = | [6 empty] | 4.8797 | [m/s]
FULL BORE DISCHARGE
Q = 785.4*D2*V
Q = 785.4*0.6^2*4.88
| FULL BORE DISCHARGE 'Q' = | [6 empty] | 1379.7039 | [litre/s]
VELOCITY OF WATER WITH REDUCED BORE DISCHARGE
Qr = γ*Q
Qr = 1,379.7 * 0.75 = 1,034.8
Vr = Qr/(785.4*D2)
Vr = 1,034.8 / (785.4 * 0.36)
| VELOCITY OF WATER FOR REDUCED BORE DISCHARGE 'Vr' = | [6 empty] | 3.6598 | [m/s]
Spreadsheet provided by: www.YourSpreadsheets.co.uk

## from author
Version: 1.1. |  |  | © 2012 Damian Janicki
| For latest updates and news visit: | Contact me at:
| www.YourSpreadsheets.co.uk | info@yourspreadsheets.co.uk
The Author takes no liability for use of this spreadsheet and gives no guarantee that it is error free. In no event shall the Author be responsible for any special, incidental or consequential damages whatsoever arising from the use of this spreadsheet, even if the Author has been advised of the possibility of such damage. This is a FREE spreadsheet. The spreadsheet can be distributed freely but only in its original form. Reverse-engineering, decompiling or disassembling of this spreadsheet is not allowable. By using this spreadsheet you understand and agree with the above terms and conditions. You also acknowledge that you do not become the owner of this spreadsheet. Damian Janicki
Changelog: 26.07.2012 - v.1.1. - official release of the spreadsheets.